| Insert Logo Here | Service Company Information (Address, Telephone, & Contact Information |  | Building Sprinkler Systems Tests |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Date of Service: |  | Last Service Date: |  |  |  |
|  |  |  | Daily | Weekly | Monthly |  |  | Quarterly |
|  |  |  | Semiannual | Annual | Third Year |  |  | Fifth Year |
| Building Name: |  |  | Contact Person: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |
| Address: |  |  | Owner/Strata Number: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |
| City: |  | Postal Code: | Central Station: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |

Summary of systems tested in accordance with the relevant Provincial Fire Code and referenced Standards.

| System |  |  |  | #1 |  | #2 |  |  | #3 |  |  |  |  | #4 | #5 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Wet |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dry pipe partial test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dry pipe full flow test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Deluge |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Pre-action |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Other |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Area of coverage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Size (gallons) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Manufacturer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| System Water Pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Supply Water Pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| System Air Pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Trip Pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Trip Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| System |  |  |  | #6 |  | #7 |  |  | #8 |  |  |  |  | #9 | #10 |  |
| Wet |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dry pipe partial test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dry pipe full flow test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Deluge |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Pre-action |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Other |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Area of coverage |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Size (gallons) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Manufacturer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| System Water Pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Supply Water Pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| System Air Pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Trip Pressure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Trip Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Yes | No | Visual Pre-Inspection Check |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Hydraulic Calculation Label in place? Date on Label: |  |  |  |  |  |  |  |  | Date of last compressor service: |  |  |  |  |  |
|  |  | Designer: |  |  |  |  |  |  |  | Engineer: |  |  |  |  |  |  |
|  |  | Corrosion evident? Sprinkler Heads Joints Hangers Supply/Riser/Distribution Piping Valves |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Corrosion is: Minor Moderate Severe Condition of heat tracing/insulation: Good Fair Poor NA |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Replacement of affected components is indicated. (“Yes” answer detailed in remarks section) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Remarks concerning the system have been made? (Please refer to the Comments/Remarks section of this report.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The information on this form (and in the pages attached here-to) attests to the fact that the equipment listed here-in was tested/inspected in conformance with applicable codes, bylaws, standards, and the manufacturer’s requirements by a qualified technician. The equipment was left in an operational condition except as noted in the spaces marked “comments”. This document has been provided to the building owner’s representative. A copy shall be maintained on the premises for examination by the Fire Marshal or Inspector at their request. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Company Name |  |  |  |  |
| Technician Performing Test |  |  |  |  | Registration Number/Stamp |  |  | Date |  |  |  | Technician Signature |  |  |  |  |

| System Number (From Summary Page): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| “” = Yes - Tested correctly “X” = No - Did not test correctly (NO answers are detailed in “Comments/Remarks”) “NA” = Not applicable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sprinkler System Inspection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Daily / weekly if low temperature alarms are installed. |  |  |  |  |  |  |  |  |  |  | Oil level in normal range on air compressor? |  |  |  |  |  |  |
|  | (a) Enclosures - dry-pipe or deluge valves maintaining 40F/4C? |  |  |  |  |  |  |  |  |  |  | Condition of oil in sight glass? Clean Cloudy Dirty |  |  |  |  |  |  |
|  | (b) Heat trace controllers’ power “on”. |  |  |  |  |  |  |  |  |  |  | Filter checked? Replacement required? Yes No NA |  |  |  |  |  |  |
|  | (c) Is heat trace controller in “trouble”? Yes No |  |  |  |  |  |  |  |  |  |  | Belt checked for proper tension? Condition? Good Worn |  |  |  |  |  |  |
|  | Weekly |  |  |  |  |  |  |  |  |  |  | Inspect electrically supervised valves? |  |  |  |  |  |  |
|  | Relief port for reduced pressure & backflow prevention assemblies |  |  |  |  |  |  |  |  |  |  | Alarm devices inspected to verify they are free from physical |  |  |  |  |  |  |
|  | is free from discharge? |  |  |  |  |  |  |  |  |  |  | damage? |  |  |  |  |  |  |
|  | Weekly and Monthly Inspection Items |  |  |  |  |  |  |  |  |  |  | Pressure regulating control valves shall be inspected. |  |  |  |  |  |  |
|  | Gauges on dry, pre-action and deluge systems in good condition? |  |  |  |  |  |  |  |  |  |  | Sprinkler pressure regulating & control valves shall be inspected. |  |  |  |  |  |  |
|  | Inspect air pressure and water pressure? |  |  |  |  |  |  |  |  |  |  | Fire department connection? |  |  |  |  |  |  |
|  | Control valves (and isolation valves on backflow prevention devices): |  |  |  |  |  |  |  |  |  |  | Annual inspection items. |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Record date of backflow internal exam. |  |  |  |  |  |  |
|  | (a) in correct (open or closed) position? |  |  |  |  |  |  |  |  |  |  | Buildings - prior to freezing weather? |  |  |  |  |  |  |
|  | (b) Sealed, locked or supervised and accessible? |  |  |  |  |  |  |  |  |  |  | Hangers and seismic braces inspected from floor level? |  |  |  |  |  |  |
|  | (c) Free from external leaks? |  |  |  |  |  |  |  |  |  |  | Pipe and fittings shall be inspected from floor level? |  |  |  |  |  |  |
|  | (d) Provided with appropriate wrenches? |  |  |  |  |  |  |  |  |  |  | Sprinklers shall be inspected from floor level? |  |  |  |  |  |  |
|  | Alarm valve free from damage, trim in correct position, and no leakage? |  |  |  |  |  |  |  |  |  |  | Spare sprinklers shall be inspected? |  |  |  |  |  |  |
|  | Quarterly Inspection Items (in addition to above) |  |  |  |  |  |  |  |  |  |  | Interior of dry pipe valve shall be inspected at time of trip test? |  |  |  |  |  |  |
|  | Pre-action and deluge valves inspected externally & free from |  |  |  |  |  |  |  |  |  |  | Pre-action/deluge valves shall be inspected internally? |  |  |  |  |  |  |
|  | damage? |  |  |  |  |  |  |  |  |  |  | Interior of dry-pipe , pre-action, deluge valves internal inspection? |  |  |  |  |  |  |
|  | Electrical components in service? |  |  |  |  |  |  |  |  |  |  | Heat Tracing - Check all connections tight, clamped & undamaged. |  |  |  |  |  |  |
|  | Gauges wet pipe in good condition and normal water pressure |  |  |  |  |  |  |  |  |  |  | Check heat trace controller for trouble and ground fault response. |  |  |  |  |  |  |
|  | is being maintained? |  |  |  |  |  |  |  |  |  |  | Check heat trace controller interconnection to fire alarm system. |  |  |  |  |  |  |
|  | Dry pipe valve/quick opening devices shall be inspected externally. |  |  |  |  |  |  |  |  |  |  | Fifth year inspection items. |  |  |  |  |  |  |
|  | Backflow prevention assemblies shall be inspected (locked or |  |  |  |  |  |  |  |  |  |  | Alarm valves & strainers, filters and restriction orifices passed |  |  |  |  |  |  |
|  | properly supervised by an acceptable electrical means). |  |  |  |  |  |  |  |  |  |  | internal inspection? |  |  |  |  |  |  |
|  | Control valves shall be inspected. |  |  |  |  |  |  |  |  |  |  | Pre-action/deluge valve and their associated strainers, filters and |  |  |  |  |  |  |
|  | Alarm valves shall be inspected externally. |  |  |  |  |  |  |  |  |  |  | restriction orifices pass internal inspection? |  |  |  |  |  |  |
|  | Hydraulic name plate is properly affixed to the sprinkler riser? |  |  |  |  |  |  |  |  |  |  | Dry pipe valves/quick opening devices internally inspect strainers, |  |  |  |  |  |  |
|  | Date on Label: |  |  |  |  |  |  |  |  |  |  | filters & orifices? |  |  |  |  |  |  |
|  | Heat Tracing - check pipe insulation for cuts or abrasions. |  |  |  |  |  |  |  |  |  |  | Check Valves internally inspected and all parts operate properly, |  |  |  |  |  |  |
|  | Check exposed cable/connectors for chaffing, cuts, or abrasions. |  |  |  |  |  |  |  |  |  |  | move freely and are in good condition? |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Interior of dry-pipe , pre-action, deluge valves internal inspection? |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Internal examination performed on Backflow Assembly? |  |  |  |  |  |  |
| Sprinkler System Testing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Quarterly Tests |  |  |  |  |  |  |  |  | Annual Testing |  |  |  |  |  |  |  |
|  |  | Water flow alarms passed tests? |  |  |  |  |  |  |  |  | Are all sprinklers in service dated 1920 or later? |  |  |  |  |  |  |  |
|  |  | Control valves opened until spring or torsion is felt in the rod? |  |  |  |  |  |  |  |  | Fast Response sprinklers in service for less than 20 yrs |  |  |  |  |  |  |  |
|  |  | Valve supervisory switches indicate movement? |  |  |  |  |  |  |  |  | If “NO” test sample now and every 10 years? |  |  |  |  |  |  |  |
|  |  | Low air pressure alarms tested in as per mfg’s requirements? |  |  |  |  |  |  |  |  | Record anti-freeze Specific Gravity: |  |  |  |  |  |  |  |
|  |  | Pre-action/deluge valves (supervised) priming water tested? |  |  |  |  |  |  |  |  | All control valves operated thru full range and returned to normal? |  |  |  |  |  |  |  |
|  |  | Alarm device, test on dry pipe, pre-action or deluge system using |  |  |  |  |  |  |  |  | Pressure regulating valve shall pass a full flow test. |  |  |  |  |  |  |  |
|  |  | bypass? |  |  |  |  |  |  |  |  | Backflow prevention assemblies have been tested by an agency |  |  |  |  |  |  |  |
|  |  | Inspectors test connection opened? (wet pipe when not freezing) |  |  |  |  |  |  |  |  | acceptable to the local authority? Date: |  |  |  |  |  |  |  |
|  |  | Bypass connection opened? (wet pipe, dry pipe, pre-action and |  |  |  |  |  |  |  |  | Forward flow test has been conducted. |  |  |  |  |  |  |  |
|  |  | deluge systems when not freezing) |  |  |  |  |  |  |  |  | Forward Flow Test results are recorded on the backflow test report? |  |  |  |  |  |  |  |
|  |  | Dry pipe valves/Quick opening devices (supervised) priming water |  |  |  |  |  |  |  |  | Standard sprinklers less than 50 yrs old. If “no” has a sample |  |  |  |  |  |  |  |
|  |  | tested for compliance with manufacturers’ instructions? |  |  |  |  |  |  |  |  | been tested within 10yrs, If “no” test sample now and every 10yrs. |  |  |  |  |  |  |  |
|  |  | Quick opening devices passed test? |  |  |  |  |  |  |  |  | Low temperature alarms in dry pipe, pre-action and deluge |  |  |  |  |  |  |  |
|  |  | Main drain test shall be conducted on each system riser. |  |  |  |  |  |  |  |  | valve enclosure passed test? |  |  |  |  |  |  |  |
|  |  | Record Static pressure: |  |  | PSIG KPAG |  |  |  |  |  | Main Drain test shall be conducted on each system riser. |  |  |  |  |  |  |  |
|  |  | Residual pressure: |  |  | PSIG KPAG |  |  |  |  |  | Record Static pressure: |  |  |  |  | PSIG KPAG |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Residual pressure: |  |  |  |  | PSIG KPAG |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Are results comparable to previous tests? |  |  |  |  |  |  |  |

| System Number (From Summary Page): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| “” = Yes - Tested correctly “X” = No - Did not test correctly (NO answers are detailed in “Comments/Remarks”) “NA” = Not applicable |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Special Suppression Systems & Additional Sprinkler System Testing Requirements |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Pre-action and deluge valve full flow trip test: (Note: Except |  |  |  |  |  |  |  |  | Auto air maintenance devices on dry pipe & pre-action passed |  |  |  |  |  |
|  | where water cannot be discharged, test all systems simultaneously.) |  |  |  |  |  |  |  |  | test? |  |  |  |  |  |
|  | Water discharge from all nozzles unimpeded? |  |  |  |  |  |  |  |  | All sprinkler pressure regulating control valves passed full flow |  |  |  |  |  |
|  | Pressure reading at |  |  |  |  |  |  |  |  | test? |  |  |  |  |  |
|  | hydraulically most remote nozzle: |  |  |  |  |  | PSIG KPAG |  |  | Dry-pipe full flow trip test (to be done every 3rd year): |  |  |  |  |  |
|  | Residual pressure reading at valve: |  |  |  |  |  | PSIG KPAG |  |  | Was water delivered to inspectors test connection? |  |  |  |  |  |
|  | Was flow observed? |  |  |  |  |  |  |  |  | Initial air pressure: |  | PSIG KPAG |  |  |  |
|  | Are above readings comparable to design values? |  |  |  |  |  |  |  |  | Water pressure: |  | PSIG KPAG |  |  |  |
|  | Manual activation devices passed test? |  |  |  |  |  |  |  |  | Trip air pressure: |  | PSIG KPAG |  |  |  |
|  | Automatic air pressure maintenance devices passed test? |  |  |  |  |  |  |  |  | Tripping time: |  | Seconds |  |  |  |
|  | Dry pipe valve partial flow trip test: |  |  |  |  |  |  |  |  | Date of trip test (from records on site) : |  |  |  |  |  |
|  |  | Initial air pressure: |  |  |  | PSIG KPAG |  |  |  | Tests to be done every fifth year: |  |  |  |  |  |
|  |  | Water pressure: |  |  |  | PSIG KPAG |  |  |  | Extra High, Very Extra High and Ultra High Temp sprinklers |  |  |  |  |  |
|  |  | Trip air pressure: |  |  |  | PSIG KPAG |  |  |  | tested? |  |  |  |  |  |
|  |  | Tripping time: |  |  |  | Seconds |  |  |  | Gauges checked against calibrated gauge or replaced? |  |  |  |  |  |
|  | Are the results comparable to previous test? |  |  |  |  |  |  |  |  | Date of service (from records on site): |  |  |  |  |  |
|  | Post indicator valves opened until spring or torsion is felt in rod. |  |  |  |  |  |  |  |  | Are above results comparable to previous tests? |  |  |  |  |  |
| Sprinkler System Maintenance Items |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Regular Maintenance Items |  |  |  |  |  |  |  | If any of the following was discovered, was an obstruction investigation conducted, and the system flushed? Yes No NA ☐ |  |  |  |  |  |  |
|  |  | If sprinklers have been replaced, were they proper replacements? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Air leaks in dry-pipe system resulting in air pressure loss more than |  |  |  |  |  |  |  |  | 1. Defective intake screen for pumps taking suction from open |  |  |  |  |  |
|  |  | 10 psi/week repaired? |  |  |  |  |  |  |  |  | sources? |  |  |  |  |  |
|  |  | Dry-pipe systems being maintained in dry condition? |  |  |  |  |  |  |  |  | 2. Obstructive material discharged during water flow tests? |  |  |  |  |  |
|  |  |  | Annual Maintenance Items |  |  |  |  |  |  |  | 3. Foreign materials found in dry-pipe valves, check valves or |  |  |  |  |  |
|  |  | Operating stem of all OS&Y valves lubricated, completely closed |  |  |  |  |  |  |  |  | pumps? |  |  |  |  |  |
|  |  | and then reopened? |  |  |  |  |  |  |  |  | 4. Heavy discoloration of water during drain test or plugging of |  |  |  |  |  |
|  |  | Interior of dry-pipe, pre-action and deluge valves cleaned? |  |  |  |  |  |  |  |  | inspector's test connection? |  |  |  |  |  |
|  |  | Low points drained in dry pipe, pre-action & deluge systems |  |  |  |  |  |  |  |  | 5. Plugging of sprinklers found during activation or alteration? |  |  |  |  |  |
|  |  | prior to freezing weather? |  |  |  |  |  |  |  |  | 6. Plugging found in piping dismantled during alterations? |  |  |  |  |  |
|  |  | Sprinklers and spray nozzles protecting commercial cooking |  |  |  |  |  |  |  |  | 7. Failure to flush yard piping or surrounding public mains |  |  |  |  |  |
|  |  | equipment and ventilating systems replaced except for bulb- |  |  |  |  |  |  |  |  | following new installation or repairs? |  |  |  |  |  |
|  |  | type which show no sign of grease buildup? |  |  |  |  |  |  |  |  | 8. Record of broken mains in the vicinity? |  |  |  |  |  |
|  |  | Temperature maintained above 10 degrees C in all sprinkler control |  |  |  |  |  |  |  |  | 9. Abnormally frequent false tripping of dry-pipe valves? |  |  |  |  |  |
|  |  | valve areas. |  |  |  |  |  |  |  |  | 10. Has system been returned to service after an extended period |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | of non-service? |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | 11. Is there reason to believe the system contains sodium silicate? |  |  |  |  |  |
| Remarks/Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |