| Insert Logo Here | Service Company Information (Address, Telephone, & Contact Information |  |  |  | Building Stand-pipe & Hose Systems Tests |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Date of Service: |  | Last Service Date: |  |  |  |  |
|  |  |  |  |  | System in service on inspection? YES NO |  | Fire Department Connection? YES NO |  |  |  |  |
|  |  |  |  |  | Control valves locked or supervised? YES NO |  | Flow switch installed? YES NO |  |  |  |  |
|  |  |  |  |  | Fire Pump installed? YES NO |  | Jockey Pump installed? YES NO |  |  |  |  |
| Building Name: |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Pressure regulating device present? YES NO |  | Hose nozzles in place? YES NO |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Length of hose provided: |  |  |  | meters feet |  |  |
| City: |  |  | Postal Code: |  | Hose is: Lined Unlined |  |  |  |  |  |  |
|  |  |  |  |  | Supply water pressure: |  |  |  |  | PSIG KPAG |  |
|  |  |  |  |  | System water pressure: |  |  |  |  | PSIG KPAG |  |
| Contact Person: |  | Phone: |  |  | Central Station: |  |  | Phone: |  |  |  |
|  |  | Fax: |  |  |  |  |  | Fax: |  |  |  |
| Owner/Strata Number: |  | Phone: |  |  | Management Company: |  |  | Phone: |  |  |  |
|  |  | Fax: |  |  |  |  |  | Fax: |  |  |  |
|  |  |  |  |  | System Class: I II III |  |  |  |  |  |  |

| Yes | No | General Observation Items: |
| --- | --- | --- |
|  |  | Is the building fully sprinklered? |
|  |  | Is the building occupied? |
|  |  | Has the occupancy classification & hazard of contents remained the same? |
|  |  | Are all existing fire protection systems in service? |
|  |  | Have modifications or renovations been done since the last inspection? |
|  |  | Have any system devices (including alarms) been actuated since the last inspection? |

“” = Yes - Tested correctly    “X” = No - Did not test correctly (NO answers are detailed in “Comments/Remarks”)     “NA” = Not applicable

| Inspection Items |  |  |  |
| --- | --- | --- | --- |
|  | Daily - Weekly |  | Hose Rack Pressure Reducing Valves: |
|  | Enclosures dry-pipe valves maintaining 4C or 40degF? |  | Hand wheel is not broken or missing? |
|  | Check relief port on pressure reducer valves are not leaking? |  | No leaks are present? |
|  | Control valves inspected for condition (“Open” or “Closed” as required). |  | Piping: |
|  | Gauges on dry system (no low pressure alarm)? |  | Piping undamaged? |
|  | Quarterly |  | Control valves undamaged? |
|  | Backflow Prevention Assembly - OS&Y valves are in the normal “Open” |  | Supervisory devices undamaged? |
|  | position? |  | No visible obstructions? |
|  | Reduced pressure assembly valves inspected for leaks or corrosion? |  | No missing or damaged pipe support devices? |
|  | Tamper switches inspected (covers secured, leaks or corrosion)? |  | Hose Connections/Valves: |
|  | Gauges to ensure good condition and normal pressure? |  | Cap in place and not damaged? |
|  | Components of standpipe system inspected? |  | Fire hose connection undamaged? |
|  | Fire department Siamese connection checked (covers in place & secure)? |  | Valve handles in place? |
|  | Hose Connection Pressure Reducing Valves: |  | Cap gaskets in place and in good condition? |
|  | Hand wheel is not broken or missing? |  | Valves not leaking? |
|  | Outlet hose threads are undamaged? |  | Restricting orifice in place? |
|  | No leaks are present? |  | Manual, semiautomatic, or dry standpipe valve operates |
|  | Reducer and cap are not missing? |  | smoothly? |

| The information on this form (and in the documents attached here-to) attest to the fact that the equipment listed here-in was tested/inspected in conformance with applicable codes, bylaws, standards, and the manufacturer’s requirements by a qualified technician. The equipment was left in an operational condition except as noted in the spaces marked “comments”. A copy should be maintained on the premises in accordance with NFC 2015 Division C Clause 2.2.1.2. |  |  |  |
| --- | --- | --- | --- |
| Company Name |  |  |  |
| Technician Performing Test | Certification No. | Date | Technician Signature |

| System Number / Identification: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| “” = Yes - Tested correctly “X” = No - Did not test correctly (NO answers are detailed in “Comments/Remarks”) “NA” = Not applicable |  |  |  |  |  |  |  |  |
| Inspection Items |  |  |  |  |  |  |  |  |
|  | Annually |  |  |  |  |  |  | Hose Storage Devices: |
|  | Hoses: |  |  |  |  |  |  | Operates easily? |
|  | Free from mildew, cuts and deterioration? |  |  |  |  |  |  | Devices undamaged, unobstructed? |
|  | Couplings of compatible threads and undamaged? |  |  |  |  |  |  | Hose properly racked or rolled? |
|  | Gaskets in place and in good condition? |  |  |  |  |  |  | Nozzle clips in place and nozzles contained? |
|  | Hose(s) connected? |  |  |  |  |  |  | Will racks swing out of the cabinet at least ninety (90) degrees? |
|  | Hose hydrostatic test dates are noted on page numbers: |  |  |  |  |  |  | Storage Cabinets: |
|  |  |  |  |  |  |  |  | Glass break device in place? |
|  | Nozzles: |  |  |  |  |  |  | Cabinets accessible and identified? |
|  | Nozzles & gaskets in place and in good condition? |  |  |  |  |  |  | All parts (valves, hoses and fire extinguishers) accessible? |
|  | No visible obstructions? |  |  |  |  |  |  | Adequate heat available to areas where wet pipe is located? |
|  | Nozzles operate smoothly? |  |  |  |  |  |  | No visible obstructions? |
|  | Nozzle is intact with no parts missing? |  |  |  |  |  |  | Cabinets have no corroded or damaged parts? |
|  | Full operation of adjustments (such as pattern selection)? |  |  |  |  |  |  | Cabinets easy to fully open? |
|  |  |  |  |  |  |  |  | Door glazing in good condition? |
|  |  |  |  |  |  |  |  | Latches functional (including break-glass type)? |
| Testing Items |  |  |  |  |  |  |  |  |
|  | Quarterly |  |  |  |  |  |  | 5 Year |
|  | Water flow alarms passed test and provide correct annunciation? |  |  |  |  |  |  | Hose Connection Pressure Reducing Valve passed flow test? |
|  | Valve supervisory switches indicate movement? |  |  |  |  |  |  | Hose Rack Assembly Pressure Reducing Valve passed flow test? |
|  | Control valves shall be opened until spring or torsion is felt in the rod? |  |  |  |  |  |  | Hydrostatic test at not less than 13.8 bar (200 psi) for 2 hours or |
|  | Jockey pump operational and in good condition? |  |  |  |  |  |  | at 3.4 bar (50 psi) in excess of maximum pressure? |
|  | Valve supervisory switches tested? |  |  |  |  |  |  | Flow Test - by flowing the required volume of water at design |
|  | Annually |  |  |  |  |  |  | pressure to the hydraulically most remote hose connection? |
|  | Control valves shall be operated through its full range and returned to |  |  |  |  |  |  | Check-valves internally inspected and all parts operate properly, |
|  | normal. |  |  |  |  |  |  | move freely, and are in good condition? |
|  | Main Drain test shall be conducted on each system riser. |  |  |  |  |  |  | Pressure control valve passed test? |
|  | Static pressure: |  | PSIG KPAG |  |  |  |  | Gauges: Tested and Calibrated Replaced |
|  | Residual pressure: |  | PSIG KPAG |  |  |  |  |  |
|  | Hose connection pressure reducing valves partial flow test. |  |  |  |  |  |  |  |
|  | Hose rack assembly pressure reducing valve partial flow test. |  |  |  |  |  |  |  |
|  | Backflow prevention assembly shall be tested at the design flow. |  |  |  |  |  |  |  |
|  | Are results comparable to previous tests? |  |  |  |  |  |  |  |

| Maintenance Items |  |  |  |
| --- | --- | --- | --- |
|  | Annually |  | Control Valves - OS&Y stems shall be lubricated? |
|  | Hose nozzles - open and close and lubricate if necessary. |  | Hose connections? |
|  | Swing out Racks - lubricate and ensure proper operation. |  | Low points in dry systems drained prior to freezing weather? |
|  | Hoses re-racked? |  | 5 Year |
|  | Interior of dry pipe valve cleaned? |  | Check valves internally inspected and operating properly? |

| Standpipe Hydrostatic and Flow Test Results (to be completed every five years) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date of last hydro-test: |  |  |  |  |  |  | Date of last flow test: |  |  |  |  |  |  |
| Start Time: |  |  | End Time: |  |  |  | Start Time: |  |  | End Time: |  |  |  |
| Initial Test Pressure: |  |  | Bar (PSI) |  |  |  | Static Pressure: |  |  | Bar (PSI) |  |  |  |
| End Test Pressure: |  |  | Bar (PSI) |  |  |  | Residual Pressure:: |  |  | Bar (PSI) |  |  |  |
|  |  |  |  |  |  |  | Pitot Pressure: |  |  | Bar (PSI) |  |  |  |
|  |  |  |  |  |  |  | Nozzle Diameter: |  |  | cm inches |  |  |  |
|  |  |  |  |  |  |  | Flow Rate: |  |  | liters/min gallons/min |  |  |  |
| Notes: - Flow tests are to be conducted from the hydraulically most remote standpipe outlet. - For Class I or III systems, the minimum flow should be 1893 liters/min (500 gallons/min) at a residual pressure of 6.9 bar (100 psi) - For Class II systems, the minimum flow should be 379 liters/min (100 gallons/min) at a residual pressure of 4.5 bar (65 psi) |  |  |  |  |  |  |  |  |  |  |  |  |  |

Comments/Remarks: